## HOT_WATER
Description | code | class_dhw | Tsww0_C | Qwwmax_Wm2
None | HVAC_HOTWATER_AS0 | NONE | 0 | 0
High temperature water (60/10) | HVAC_HOTWATER_AS1 | HIGH_TEMP | 60 | 500
Medium temperature water (45/10) | HVAC_HOTWATER_AS2 | MEDIUM_TEMP | 45 | 500
Low temperature water + sanitation (35/10) | HVAC_HOTWATER_AS3 | LOW_TEMP | 35 | 500
High temperature in the tropics (60/25) | HVAC_HOTWATER_AS4 | HIGH_TEMP | 60 | 500

## HEATING
Description | code | class_hs | convection_hs | Qhsmax_Wm2 | dThs_C | Tshs0_ahu_C | dThs0_ahu_C | Th_sup_air_ahu_C | Tshs0_aru_C | dThs0_aru_C | Th_sup_air_aru_C | Tshs0_shu_C | dThs0_shu_C
None | HVAC_HEATING_AS0 | NONE | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | NA
Radiator (90/70) | HVAC_HEATING_AS1 | RADIATOR | 1 | 500 | 0.15 | NA | NA | NA | NA | NA | NA | 90 | 20
Radiator (70/55) | HVAC_HEATING_AS2 | RADIATOR | 1 | 500 | -0.1 | NA | NA | NA | NA | NA | NA | 70 | 15
central AC (40/20) | HVAC_HEATING_AS3 | CENTRAL_AC | 1 | 500 | -1.1 | 40 | 20 | 36 | 40 | 20 | 36 | NA | NA
Floor heating (40/35) | HVAC_HEATING_AS4 | FLOOR_HEATING | 0.5 | 150 | -0.9 | NA | NA | NA | NA | NA | NA | 40 | 5

## COOLING
Description | code | class_cs | convection_cs | Qcsmax_Wm2 | dTcs_C | Tscs0_ahu_C | dTcs0_ahu_C | Tc_sup_air_ahu_C | Tscs0_aru_C | dTcs0_aru_C | Tc_sup_air_aru_C | Tscs0_scu_C | dTcs0_scu_C | References
none | HVAC_COOLING_AS0 | NONE | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | NA | NA
ceiling cooling (18/21) | HVAC_COOLING_AS1 | CEILING_COOLING | 0.5 | 500 | 0.5 | NA | NA | NA | NA | NA | NA | 18 | 3
mini-split AC (6/15) | HVAC_COOLING_AS2 | DECENTRALIZED_AC | 1 | 150 | 0.7 | NA | NA | NA | 6.5 | 9 | 16 | NA | NA
central AC (6/15) | HVAC_COOLING_AS3 | CENTRAL_AC | 1 | 500 | 0.5 | 6.5 | 9 | 13 | 6.5 | 9 | 13 | NA | NA | supply air temperatures of ahu and aru accroding to Ashrae 90.1 (55F)
3for2 | HVAC_COOLING_AS4 | HYBRID_AC | 1 | 500 | 0.5 | 6.5 | 7 | 18 | 6.5 | 4 | 13 | 18 | 3 | supply air temperatures of ahu and aru accroding to Ashrae 90.1 (55F)
floor cooling (18/21) | HVAC_COOLING_AS5 | FLOOR_COOLING | 0.1 | 100 | 0.5 | NA | NA | NA | NA | NA | NA | 18 | 3

## VENTILATION
Description | code | MECH_VENT | WIN_VENT | HEAT_REC | NIGHT_FLSH | ECONOMIZER
Window ventilation | HVAC_VENTILATION_AS0 | FALSE | TRUE | FALSE | TRUE | FALSE
Mechanical ventilation with demand control | HVAC_VENTILATION_AS1 | TRUE | FALSE | TRUE | TRUE | FALSE
Mechanical ventilation with demand control and economizer | HVAC_VENTILATION_AS2 | TRUE | FALSE | TRUE | TRUE | TRUE
Window ventilation - no night flushing | HVAC_VENTILATION_AS3 | FALSE | TRUE | FALSE | FALSE | FALSE

## CONTROLLER
Description | code | dT_Qhs | dT_Qcs
None | HVAC_CONTROLLER_AS0 | 2.5 | -2.5
None | HVAC_CONTROLLER_AS1 | 2.5 | -2.5
PI controller | HVAC_CONTROLLER_AS2 | 1.2 | -1.2
PI controller with optimum tuning | HVAC_CONTROLLER_AS3 | 0.9 | -0.9
room temperature control (electromagnetically/electronically). | HVAC_CONTROLLER_AS4 | 1.8 | 1.8